- GENERAL

  - GENERAL INSTRUCTIONS

    - Read and conform to Division 1 requirements and documents referred to therein.

  - SUMMARY

    - Section Includes: Provide PVC roofing mechanically fastened including but not limited to following:

      - roof sheathing.

      - vapour retarder.

      - roof insulation.

      - single ply PVC roofing membrane and flashings.

      - roof drains.

      - roof expansion joints.

      - roof walkways.

    - Related Sections: Following description of work is included for reference only and shall not be presumed complete:

      - Reglets, through wall flashings and air/vapour barrier installation: Section 04 20 00, Masonry Units.

      - Metal deck, roof sump pans and metal curbs: Section 05 30 00, Metal Decking.

      - Plywood and wood framing: Section 06 10 00, Rough Carpentry.

      - Supply of prepainted flashings: Section 07 62 00, Sheet Metal Flashing and Trim.

      - Sealants except for sealant required for roof flashings: Section 07 92 00, Joint Sealants.

      - Skylights: Section 08 62 00, Unit Skylights.

      - Provision of roof drains: Division 22, Plumbing.

      - Prefabricated curbs for mechanical equipment on roof and counter flashings for ducts passing through roof: Division 23, Heating, Ventilating and Air Conditioning.

  - REFERENCES

    - Abbreviations and Acronyms:

      - CaGBC: Canadian Green Building Council; www.cagbc.org.

      - CRCA: Canadian Roofing Contractors’ Association; www.roofingcanada.com.

      - FM: Factory Mutual Global; www.fmglobal.com.

      - LEED®: Leadership in Energy and Environmental Design; www.cagbc.org.

      - LTTR: Long Term Thermal Resistance.

      - PVC: Polyvinyl Chloride.

      - SRI: Solar Reflectance Index.

      - ULC: Underwriters Laboratories of Canada; www.ulc.ca.

      - ULE: UL Environment; www.ulenvironment.com.

      - CSA: CSA Group; www.csagroup.org

    - Definitions: Conform to ASTM D1079 for glossary of terms and definitions of roofing terminology.

    - Reference Standards:

      - ASTM C1177/C1177M-08	- Standard Specification for Glass Mat Gypsum Substrate for       				Use as Sheathing

      - ASTM D1079-10		- Standard Terminology Relating to Roofing, Waterproofing,          				and Bituminous Materials

      - ASTM D3273-00(05)	- Standard Test Method for Resistance to Growth of Mold on   	 			the Surface of Interior Coatings in an Environmental   	            				Chamber

      - ASTM E84-10b		- Standard Test Method for Surface Burning Characteristics of     				Building Materials

      - ASTM E96/E96M-05	- Standard Test Methods for Water Vapor Transmission of        				Materials

      - ASTM E136-11		- Standard Test Method for Behavior of Materials in a Vertical    				Tube Furnace at 750°C

      - CAN/CGSB-51.34-M86	- Vapour Barrier, Polyethylene Sheet for Use in Building            				Construction

      - CSA B111-74(03)		- Wire Nails, Spikes and Staples

      - FM 4450-89			- Approval Standard for Class 1 Insulated Steel Deck Roofs

      - FM 4470-10			- Approval Standard for Single-Ply, Polymer-Modified Bitumen
 				Sheet, Built-Up Roof (BUR) and Liquid Applied Roof
 				Assemblies for use in Class 1 and Noncombustible Roof Deck
 				Construction

      - UL 1256			- Fire Test of Roof Deck Constructions

      - CAN/ULC-S102-07		- Standard Method of Test for Surface Burning Characteristics  				of Building Materials and Assemblies

      - CAN/ULC-S107-03		- Standard Methods of Fire Tests of Roof Coverings

      - CAN/ULC-S114-05		- Standard Method of Test for Determination of Non-                 				Combustibility in Building Materials

      - CAN/ULC-S126-06		- Standard Method of Test for Fire Spread Under Roof-Deck       				Assemblies

      - CAN/ULC-S704-03		- Standard for Thermal Insulation, Polyurethane and                    				Polyisocyanurate, Boards, Faced

      - CAN/ULC-S770-03		- Standard Test Method for Determination of Long-Term               				Thermal Resistance of Closed Cell Thermal Insulating Foams

      - CAN/CSA-A123.21		- Standard Test Method for Dynamic Wind Uplift Resistance of                                              Membrane-Roofing Systems

  - ADMINISTRATIVE REQUIREMENTS

    - Preinstallation Meetings:

      - Arrange preinstallation meeting 1 week prior to commencing work with all parties associated with trade as designated in Contract Documents or as requested by Consultant. Presided over by Contractor, include Consultant who may attend, Subcontractor performing work of this trade, Owner’s representative, testing company's representative and consultants of applicable discipline. Review Contract Documents for work included under this trade and determine complete understanding of requirements and responsibilities relative to work included, storage and handling of materials, materials to be used, installation of materials, sequence and quality control, Project staffing, restrictions on areas of work and other matters affecting construction, to permit compliance with intent of work of this Section.

      - Review installation procedures and coordination required with related work including roofing requirements for interfacing with roof accessories and roof mounted equipment.

      - Review methods and procedures related to roofing installation, including manufacturer's written instructions.

      - Review and finalize construction schedule and verify availability of materials, installer's personnel, equipment and facilities needed to make progress and avoid delays.

      - Examine deck substrate conditions and finishes for compliance with requirements, including flatness and fastening.

      - Review structural loading limitations of roof deck during roofing.

      - Review base flashings, special roofing details, roof drainage, roof penetrations, equipment curbs, and condition of other construction that will affect roofing system.

      - Review temporary protection requirements for roofing system during and after installation.

      - Review roof observation and repair procedures after roofing installation.

    - Scheduling:

      - Co-operate fully with other Subcontractors on the Work and promptly proceed with this work as rapidly as job conditions permit.

      - Supply items to be built in, in ample time to be incorporated into work of other Subcontractors as it is carried up. Proceed with insulation, roofing and flashing work as soon as walls and roof decks are ready to receive same.

  - SUBMITTALS

    - Product Data:  Submit Product data on membrane, insulation, flashing materials and roof accessories.

    - Shop Drawings:

      - Submit Shop Drawings in accordance with Section 01 30 00 showing method of installation and layout of each layer, fastening and flashings at edges, flashing of protrusions and penetrations, details of insulation and vapour retarder and securement details of sheathing.

      - Ensure Shop Drawings are approved and signed by manufacturer's representative.

    - Samples: Submit samples in accordance with Section 01 30 00. Submit following samples in sizes indicated:

      - insulation 150 mm x 150 mm (6" x 6") square.

      - roof membrane 215 mm x 280 mm (8-1/2" x 11") square.

    - Test and Evaluation Reports:

      - Provide Product certification of compliance to fire and wind uplift resistance based on evaluation of comprehensive test performed by manufacturer and witnessed by a qualified independent testing agency for components of roofing system.

      - Indicate components of roofing system comply with requirements of these Specifications including quantity, statistical and descriptive data for each Product.

    - Special Procedure Submittals: Submit Notice of Award to Sika’s Technical Department minimum 2 weeks prior to start of Project. No material will be shipped until Notice of Award is submitted and approved by Sika’s Technical Department.

  - CLOSEOUT SUBMITTALS

    - Operational and Maintenance Data:

      - Supply necessary maintenance data and repair instructions for binding into maintenance manuals described in Section 01 70 00.

      - Bind into each maintenance manual, Project name, location, dated and executed copy of manufacturer's guarantee, described herein and name, address and phone number of nearest manufacturer's representative.  Include recommendations for periodic inspections, care and maintenance.  Identify common causes of damage with instructions for temporary patching until permanent repair can be made.

  - QUALITY ASSURANCE

    - Qualifications:

      - Manufacturer:

        - Ensure manufacturer is a member in good standing a member of CaGBC.

        - Ensure membrane manufacturer is able to show Owner or Consultant an existing operational PVC roof system supplied by same manufacturer that has been operational for a minimum of 20 years.

        - Ensure membrane manufacturer is able to show Owner or Consultant a reference service life for the roofing system of a minimum 35 years.

        - Ensure membrane manufacturer is able to provide certification by ULE that roofing membrane has a minimum 10% recycled content.

        - Ensure membrane manufacturer has a recycling program in place to recycle PVC roofing products provided in roofing system.

      - Installers:

        - Ensure roofing applicator is a member in good standing with CRCA and has a minimum of 5 years experience in installing single-ply roofing and has specialized equipment in proper operating condition to perform work in accordance with manufacturer's printed instructions.

        - Ensure applicator is trained and approved by manufacturer of system being installed.

    - Conform to CRCA’s “Roofing Specifications” and Manufacturer’s manual as amended to date of this Specification, except where indicated or specified otherwise. Do roofing work employing roofing Products, [roof sheathing,] plates and fasteners conforming to FM data for proposed roofing system. More stringent requirements in Consultant’s opinion governs.

    - Conform to CRCA’s “Roofing Specifications” and Manufacturer’s manual as amended to date of this Specification, except where indicated or specified otherwise.

    - Do roofing work employing roofing Products, [roof sheathing,] plates and, fasteners, insulation and membrane as defined by ULC, CAN/CSA-A123.21 and or FM Approvals.

    - More stringent requirements in Consultant’s opinion shall govern.

    - This roofing system shall be applied only by a Roofing Contractor authorized by the manufacturer.

    - Manufacturer will provide periodic site reviews of the installation.

    - Any deficiencies indicated in the periodic site reviews shall be corrected in a timely matter.

  - DELIVERY, STORAGE AND HANDLING

    - Delivery and Acceptance Requirements: Deliver materials undamaged in original containers with manufacturer's labels and seals intact.

    - Storage and Handling Requirements:

      - Store materials undamaged in original containers with manufacturer's labels and seals intact.  Store membrane rolls flat and protected from moisture.

      - Store solvent-based liquids, adhesives and sealants away from excessive heat and open flames and at temperatures between 15 deg C (59 deg F) and 26 deg C (79 deg F). Contact adhesives and cleaning fluids are extremely flammable, avoid open flame and sparks. Smoking is prohibited in area of roofing application. Contact adhesives contain petroleum distillates; avoid breathing vapours and provide adequate ventilation when using same within enclosed areas.

- Delete roof sheathing if no metal deck or its not required.

      - Do not expose insulation [and roof sheathing] to wet weather. Store and handle insulation to prevent broken edges and corners, punctures, indentations or other damage. Remove damaged insulation from site.

      - Store materials at site within temporary sheds or trailers; such facilities must be well sealed and kept at least 3 deg C (5 deg F) warmer than exterior ambient temperature to ensure materials remain dry in terms of roofing. Do not use wet, damp, frozen or damaged materials. Stack rolls of felt on end.

      - Do not store more than 1 Day's supply of materials on the roof at any time. On roof, stack materials on pallets, and completely cover with incombustible waterproof tarpaulin whenever work is interrupted, or when there is precipitation of any kind. Securely tie covering to pallets in such way as to be weathertight.  Plastic covers and shrinkwrap covers by manufacturers are not acceptable for site storage and be removed upon delivery to roof.

      - Distribute materials stored on roof to stay within designated live load limits of the roof construction. Provide ample bases under equipment and materials to distribute weight to conform to these live-load limits. Do not store materials on, or transport materials across, completed roof areas.

      - Provide fire extinguishers at each installation and storage location, of proper type for materials being used and stored.

  - SITE CONDITIONS

    - Ambient Conditions: Do not install materials in rain, cold, moisture, frost, snow or other climatic conditions which could jeopardize proper application of materials. Refer to and comply with manufacturer's recommendations and limitations relative to this subject.

  - WARRANTY

    - Manufacturer Warranty:

- Select the Sika warranty type and warranty duration. Refer to Sika Canada Inc for samples of the warranties.

- For 25- and 30-year warranties, refer to SPEC NOTES and or contact membrane manufacturer’s technical department for special requirements.

      - Upon substantial completion Sika Canada Inc. warrants to the Owner the specified warranty type for the specified warranty duration. The roofing is installed according to Sika’s Technical instructions by a Sika Authorized Roofing Applicator. The warranty must be non-prorated and must not exclude coverage due to ponding water.

      - Warranty Type:

        - Sarnafil System

        - Sarnafil Standard

        - Sarnafil Membrane

      - Warranty duration:

        - 5 years

        - 10 years

        - 15 years

        - 20 years

        - 25 years

        - 30 years

    - Contractor Warranty:

      - Upon substantial completion the Contractor warrants to the Owner a written warranty covering defects in workmanship for a period not less than 2 years as per CRCA or the Provincial affiliate. The warranty document is on CRCA’s or the Provincial affiliates standard form.

- PRODUCTS

  - MANUFACTURERS

    - Manufacturer List: Products of following manufacturers are acceptable subject to conformance to requirements of Drawings, Schedules and Specifications:

      - Sika; www.sika.ca

  - MATERIALS

    - Description:

      - Regulatory Requirements:

- Under ULC, roofing assemblies shall have fire resistant properties that enable them to resist flames from sources outside the building (e.g., flames or hot brands from near by fire) in addition to other Code requirements that require fire resistance to fires originating inside the building.

- Roof coverings are 2 types, built-up and prepared and are intended for protection of decks from external fire exposure. Membranes have been tested to CAN/ULC-S107 over noncombustible decks. Roof coverings under this classification are not evaluated for performance when exposed to fore from internal source. Verify for authorities having jurisdiction as to which class of roof coverings will be acceptable in each location.

- Class A includes roof coverings which are effective against severe fire exposures; coverings are not readily flammable and do not carry or communicate fire, afford high degree of protection to deck; do not slip from position; possess no flying-brand hazard; and do not require frequent repairs in order to maintain their fire resistance properties.

- Class B includes roof coverings which are effective against moderate fire exposures; coverings are not readily flammable and do not carry or communicate fire, afford moderate degree of protection to deck; do not slip from position; possess no flying-brand hazard; but may require infrequent repairs in order to maintain their fire resistance properties.

- Class C includes roof coverings which are effective against light fire exposures; coverings are not readily flammable and do not readily slip from position; possess no flying-brand hazard; and may require occasional repairs in order to maintain their fire resistance properties.

        - Fire Hazard Classification: ULC Class [A] [B] [C]. Ensure complete roof meets ULC requirements for Class [A] [B] [C], as applicable, roof and other authorities having jurisdiction.

- Delete reference to FM if not required.

        - FM: Ensure roofing and flashing membranes comply with FM 4470, single ply (PVC) roofing system complies with FM 4450 as part of roofing assembly listed in FM Approval Guide for as applicable for Windstorm Classification [1-60] [1-75] [1-90] [1-105] [1-120] etc.

        - System shall meet wind load requirements in accordance with NBCC’s Limit States design requirement, (NBCC - Subsections: 4.1.3 and 4.1.7).

          - Field Pressure (___)

          - Perimeter/Edge Pressure (___), Perimeter/Edge End Zone width, Z (___)

          - Corner Pressure (___), Corner End Zone width, Z (___)

        - Wind Uplift Resistance: Ensure roofing when tested to FM 4470 or CAN/CSA-A123.21 meets or exceeds the specified wind load.

    - Performance/Design Criteria:

      - Roofing System: PVC mechanically fastened membrane roofing system [conforming to standards set out in Canadian Green Building Council LEED® Green Building Rating System Canada] consisting of following without limitation:

- Edit in accordance with materials listed in Part 2.

        - decking (by others).

        - roof sheathing.

        - vapour retarder.

        - insulation.

        - roofing membrane (PVC).

        - roof flashings.

        - roof walkways.

- Use over steel deck as a substrate for vapour retarder. Check thickness indicated on Drawings. Use silicone free boards for automotive plants and other areas where silicone is undesirable.

    - Roof Sheathing: Supply gypsum glass mat reinforced silicone treated [silicone free] board conforming to ASTM C1177/C1177M, non combustible according to ASTM E136/CAN/ULC-S114 thermal barrier as tested to UL 1256/CAN/ULC-S126, flame spread 0, smoke developed 0 to ASTM E84/CAN/ULC-S102 and ASTM D3273 with a rating of 10, no mould growth after 4 weeks exposure, 12.7 mm (1/2") thick gypsum board 1200 mm (4') wide, maximum practical length, tapered edge as required, "DensDeck (Prime)” or for fire rating requirement 15.9 mm (5/8") thick gypsum board 1200 mm (4') wide, maximum practical length, tapered edge as required, "DensDeck (Prime) Fireguard" by Georgia-Pacific Canada, Inc., supplied by Sika Sarnafil.

- Sarnavap 6 only applicable for warranties up to 20 years.

    - Vapour Retarder:

      - Vapour Retarder: "Sarnavap 6" by Sika, 0.15 mm (6 mil) low density polyethylene sheet in accordance with CGSB 51.34-M86.

      - Vapour Retarder: "Sarnavap 10" by Sika, 0.25 mm (10 mil) low density polyethylene sheet with permeance of 1.07 ng/(Pa•s•m2) (0.019 perms) in accordance with ASTM E96 and air flow rate of <0.0002 L/s∙m2 (<0.00004 cfm/ft2) in accordance with ASTM E2178.

      - Vapour Retarder: Provide "Vapour Retarder SA 31” with “Vapor Retarder Primer” by Sika, 0.8 mm (31 mil) thick self-adhesive vapor retarder/air barrier with water vapor permeance of 1.04 ng/(Pa•s•m2) (0.018 perms) in accordance with ASTM E96 and air flow rate of <0.0003 L/s∙m2 (<0.00006 cfm/ft2) in accordance with ASTM E2178.

      - Vapour Retarder: Provide "Vapour Retarder SA 106” with “Vapor Retarder Primer” by Sika, 2.7 mm (106 mil) thick self-adhesive vapor retarder/air barrier with water vapor permeance of .543 ng/(Pa•s•m2) (0.010 perms) in accordance with ASTM E96, and air flow rate of <0.0004 L/s∙m2 (<0.00008 cfm/ft2) in accordance with ASTM E2178.

      - Vapour Retarder: Provide "Vapour Retarder TA 138” with “Vapour Retarder Primer” by Sika, 3.5 mm (138 mil) thick torch applied vapour retarder/air barrier with water vapour permeance of .32 ng/(Pa•s•m2) (0.006 perms) in accordance with ASTM E96, and air flow rate of <0.0003 L/s∙m2 (<0.00003 cfm/ft2) in accordance with ASTM E2178.

- Vapor Retarder TA 138 is applicable for installation on concrete decks or over Roof Sheathing as specified  above.

- Select the Rigid Polyisocyanurate and / or Rigid Dual Density Stone Wool insulation. If a hybrid insulation strategy (combination of Rigid Polyisocyanurate and Rigid Dual Density Stone Wool insulation) is used the Rigid Polyisocyanurate is to be installed as the base layer and the Rigid Dual Density Stone Wool insulation is to be installed as the top layer.

- Type 2 (140 kpa, 20 psi)

    - Insulation:

      - Rigid Polyisocyanurate Insulation Boards: “Sarnatherm (20 psi) and Sarnatherm Tapered (20 psi)” by Sika, Square edged, closed cell polyisocyanurate foam manufactured with no CFCs or HCFCs, Zero Ozone Depleting Potential and integrally laminated to fibre reinforce felt facers, meeting requirements of CAN/ULC-S704, Type 2 with a minimum compressive strength of 140 kPa (20 psi), CAN/ULC-S126-M and CAN/ULC-S107. Approved and listed by Factory Mutual Global and CSA A123.21 for applicable windstorm classification and conforming FM4450/4470 approval requirements for Class 1 Fire as a component in roof deck construction. R-value LTTR determined in accordance with CAN/ULC-S770 and following:

- For a 25 and 30 year warranty insert the following paragraph in lieu of the previous paragraph

      - Rigid Polyisocyanurate Insulation Boards: “Sarnatherm CG (20 psi) and Sarnatherm Tapered CG (20 psi)” by Sika, Square edged, closed cell polyisocyanurate foam manufactured with no CFCs or HCFCs, Zero Ozone Depleting Potential and integrally laminated to coated glass facers, meeting requirements of CAN/ULC-S704, Type 2 with a minimum compressive strength of 140 kPa (20 psi), CAN/ULC-S126-M and CAN/ULC-S107. Approved and listed by Factory Mutual Global and CSA A123.21 for applicable windstorm classification and conforming FM4450/4470 approval requirements for Class 1 Fire as a component in roof deck construction. R-value LTTR determined in accordance with CAN/ULC-S770 and following:

- Type 3 (175 kpa, 25psi)

      - Rigid Polyisocyanurate Insulation Boards: “Sarnatherm (25 psi) and Sarnatherm Tapered (25 psi)” by Sika, Square edged, closed cell polyisocyanurate foam manufactured with no CFCs or HCFCs, Zero Ozone Depleting Potential and integrally laminated to fibre reinforce felt facers, meeting requirements of CAN/ULC-S704, Type 3 with a minimum compressive strength of 175 kPa (25 psi), CAN/ULC-S126-M and CAN/ULC-S107. Approved and listed by Factory Mutual Global and CSA A123.21 for applicable windstorm classification and conforming FM4450/4470 approval requirements for Class 1 Fire as a component in roof deck construction. R-value LTTR determined in accordance with CAN/ULC-S770 and following:

- For a 25- and 30-year warranty insert the following paragraph in lieu of the previous paragraph

      - Rigid Polyisocyanurate Insulation Boards: “Sarnatherm CG (25 psi) and Sarnatherm Tapered CG (25 psi)” by Sika, Square edged, closed cell polyisocyanurate foam manufactured with no CFCs or HCFCs, Zero Ozone Depleting Potential and integrally laminated to coated glass facers, meeting requirements of CAN/ULC-S704, Type 3 with a minimum compressive strength of 175 kPa (25 psi), CAN/ULC-S126-M and CAN/ULC-S107. Approved and listed by Factory Mutual Global and CSA A123.21 for applicable windstorm classification and conforming FM4450/4470 approval requirements for Class 1 Fire as a component in roof deck construction. R-value LTTR determined in accordance with CAN/ULC-S770 and following:

- Insert the Total R-value required or note as per Architectural Drawings

        - Total R-value of (Insert Total R-value) for insulation and insulation overlay board combined (excluding tapered insulation).

        - Multiple layers of insulation are required when the specified R-value requires an insulation thickness greater than 2.7” thick.

        - Dimension Stability: 2% maximum linear change when conditioned at 70 deg C (158 deg F) and 97% relative humidity for 7 Days; curing time 24 hours minimum, plus an additional 24 hours minimum per inch (25 mm) of thickness, at a minimum of 16 deg C (60 deg F) before shipment from manufacturer.

        - Ensure maximum insulation board size is 1200 mm x 2400 mm (4' x 8').

        - Ensure insulation is without limitations devoid of face-sheet delamination, edge cavitation, cupping, bowing, crushing or powdering.

- Applicable for all warranties. A coverboard is required.

      - Rigid Dual Density Stone Wool roof insulation board, Supplied by Sika, manufactured from basalt rock and steel slag in compliance with ASTM C726. Non-combustible in accordance with CAN/ULC S114. Class 1-NCC (non-combustible core) rated roof insulation in accordance with FM Approval 4450/4470. Thermal resistance determined in accordance with ASTM C518 and following:

- Insert the Total R-value required or note as per Architectural Drawings

        - Total R-value of (Insert Total R-value) for insulation and insulation overlay board combined (excluding tapered insulation).

        - Thermal resistance to ASTM C518:

          - R-value 3.8 hr.ft².F/Btu / RSI 0.68 m2K/W 	at 25 ºC.

          - R-value 4.3 hr.ft².F/Btu / RSI 0.72 m2K/W at - 4 ºC.

          - R-value 3.6 hr.ft².F/Btu / RSI 0.64 m2K/W at 43 ºC.

        - Water absorption of less than 1.0 % in accordance with ASTM C209

        - Minimum board thickness: 50 mm (2 inches)

        - Recycled content: 40 % minimum

- Use silicone free boards for automotive plants and other areas where silicone is undesirable.

- Insulation Overlay Board is required for 25 and 30 year warranties.

    - Insulation Overlay Board:

      - Insulation Overlay Board: “Sarnatherm Roof Board A-III” by Sika, High-density polyisocyanurate roof board with coated glass facers, conforming to ASTM C1289, Type II, Class 4, Grade 1, 12.5 mm (1/2"), thick board 1200 mm x 2400 mm (4' x 8'), compressive strength of minimum 550 kPa (80 psi) to 760 kPa (110 psi), R-Value of 2.5 based on ASTM C18.

      - Insulation Overlay Board: Supply gypsum glass mat reinforced silicone treated [silicone free] board conforming to ASTM C1177/C1177M, non-combustible according to ASTM E136/CAN/ULC-S114 thermal barrier as tested to UL 1256/CAN/ULC-S126, flame spread 0, smoke developed 0 to ASTM E84/CAN/ULC-S102 and ASTM D3273 with a rating of 10, no mould growth after 4 weeks exposure, 6.4 mm (1/4"), 12.7 mm (1/2"), 15.9 mm (5/8") thick gypsum board 1200 mm (4') wide, maximum practical length, tapered edge as required, " DensDeck Prime" by Georgia-Pacific Canada, Inc., supplied by Sika.

    - Fasteners:

      - Fasteners and pressure distribution plate to meet Factory Mutual 4470 and CSA A123.21 for wind uplift requirements. Factory-coated steel fasteners and metal or plastic plates meeting corrosion-resistance provisions in FM 4470; designed for fastening roofing membrane components to substrate; tested by manufacturer for required pullout strength; and acceptable to roofing system manufacturer. Ensure fasteners engage in the deck as per manufacturer’s requirements.

- Select the appropriate fasteners for the application / deck type.

      - "Sarnafastener #15 XP” by Sika, threaded drill point, corrosion-resistant fastener, used for attaching S327 roof membrane to steel decking (18-24 gauge), wood plank (min. 2”) or wood sheathing (min 3/4”). May also be used to attach insulation, overlay boards.

      - "Sarnafastener #14” by Sika, threaded drill point, corrosion-resistant fastener, used for attaching S327 roof membrane to concrete decking (3000 psi), wood plank (min. 2”) or wood sheathing (min 3/4”). May also be used to attach insulation, overlay boards.

      - "Sarnafastener #12" by Sika, threaded drill point, corrosion-resistant fastener, used for attaching insulation, overlay boards to steel decking (18-24 gauge), wood plank (min. 2") or wood sheathing (min 3/4").

      - "Sarnaplate" by Sika, corrosion-resistant 3” square metal plate for attaching insulation, overlay boards.

- Select the appropriate inseam load distribution plate / bar.

      - “Sikaplan Disc” by Sika, round steel plate with eyehooks, corrosion-resistant metal distribution plate for attaching S327 membrane in-seam, to roof decks, with a single weld and base fixation attachment.

      - Screws: Zinc and dichromate plated.

      - Nails: Non-ferrous or galvanized steel, flat head, barbed roofing nails. CSA B111, Table 12, size and type to suit application.

      - Metal Discs:  Flat caps of 25 mm (1") minimum diameter, 0.759 mm (22 ga) minimum sheet metal, formed to prevent dishing. No discs are required with roofing nails having 25 mm (1") diameter solid cap heads.

- Roofing Membrane only, for a 20 year or less warranty the minimum membrane thickness is 1.5 mm (60 mil), for a 25-year warranty the minimum membrane thickness of 1.8 mm (72 mil) and for a 30-year warranty the minimum membrane thickness of 2.0 mm (80 mil).

- Select the roofing membrane. Remove [Feltback] if not applicable.

- Recycled Content apply to 5 ft. and 10 ft, wide membranes.

    - Roofing Membrane:

      - Roofing Membrane: "Sarnafil Type S327 [Feltback] EnergySmart" by Sika, 1.5 m (5 ft.) or 3 m (10ft.) wide, lacquer coated, polyester reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane [colour White, with a minimum 3-year aged SRI of 0.93], [colour Reflective Grey, with a minimum 3-year aged SRI of 0.78]. Minimum Certified Thickness [1.5 mm (60 mil)] [1.8 mm (72 mil)] [2.0 mm (80 mil)].

      - Roofing Membrane: "Sarnafil Type S327 Textured" by Sika, 3 m (10ft.) wide, polyester reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane, colour Reflective Grey. Minimum Certified Thickness [1.5 mm (60 mil)][2.0 mm (80 mil).

      - Roofing Membrane: "Sarnafil Type S327 Textured" by Sika, 2 m (6.56 ft.) wide, lacquer coated, polyester reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane, colour White or Reflective Grey. Minimum Certified Thickness [1.5 mm (60 mil)] [1.8 mm (72 mil)] only available in Grey] [2.0 mm (80 mil) only available in Grey].

- Recycled Content apply to 5 ft. and 10 ft, wide membranes.

- The roofing membrane shall conform to:

      - NSF/ANSI Standard 347, "Sustainability Assessment for Single Ply Roofing Membranes". Certification Level: Platinum.

      - Recycled Content: 9% Pre-Consumer and 1% Post-Consumer

      - The manufacture to guarantee that the membrane thickness meets or exceeds [the specified thickness] when tested according to ASTM D751 [1.5 mm (60 mil)] [1.8 mm (72 mil)] [2.0 mm (80 mil)].

- Select Flashing membrane.

    - Flashing Membrane:

      - Flashing Membrane: "Sarnafil Type G410 EnergySmart" by Sika, 1.5 m (5 ft.) or 3 m (10ft.) wide, lacquer coated, non-woven glass fibre reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane [colour White or Reflective Grey]. Minimum Certified Thickness [1.5 mm (60 mil)] [1.8 mm (72 mil)] [2.0 mm (80 mil)].

      - Flashing Membrane: "Sarnafil G410 SA EnergySmart" by Sika, 2 m (6.56 ft.) wide, with a factory applied pressure‐sensitive adhesive backing and siliconized polyethylene release liner, lacquer coated, non-woven glass fibre reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane, [colour White, with a minimum 3-year aged SRI of 0.90], [colour Reflective Grey, with a minimum 3-year aged SRI of 0.78]. Minimum Certified Thickness 1.5 mm (60 mil).

      - Flashing Membrane: "Sarnafil G410 Textured" by Sika, 2 m (6.56 ft.) wide, non-woven glass fibre reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane, [colour, White or Reflective Grey]. Minimum Certified Thickness 1.5 mm (60 mil).

      - Flashing Membrane: "Sarnafil G410 Textured SA" by Sika, 2 m (6.56 ft.) wide, with a factory applied pressure‐sensitive adhesive backing and siliconized polyethylene release liner, lacquer coated, non-woven glass fibre reinforced, ultra-violet light resistant, polyvinyl chloride elastomeric sheet membrane, [colour, Whiteor Reflective Grey]. Minimum Certified Thickness 1.5 mm (60 mil).

      - Flashing Membrane: “G459 Flashing Membrane” by Sika, 2m and 1 m (6.5 ft. and 3.25 ft.) wide lacquer coated, non-woven glass fibre reinforced adhered to asphalt, other contaminated surfaces, or approved substrates using Sarnacol adhesive.  Colour is white on tan.  The tan side of the membrane must be the side exposed to the contamination. Minimum Certified Thickness 1.5 mm (60 mil).

- Recycled Content apply to 5 ft. and 10 ft, wide membranes.

- The flashing membrane shall conform to:

      - NSF/ANSI Standard 347, "Sustainability Assessment for Single Ply Roofing Membranes". Certification Level: Platinum.

      - Recycled Content: 9% Pre-Consumer and 1% Post-Consumer

      - The manufacture to guarantee that the membrane thickness meets or exceeds [the specified thickness] when tested according to ASTM D751 [1.5 mm (60 mil)] [1.8 mm (72 mil)] [2.0 mm (80 mil)].

- Select flashing membrane adhesive. Not applicable “Sarnafil G410 SA (SELF‐ADHERED) EnergySmart” roofing membrane.

    - Flashing Membrane Adhesive: "Sarnacol 2170R or 2170VC Adhesive" by Sika, is a solvent-based reactivating adhesive used for adhering flashing membranes.  Sarnacol 2170 is formulated for adhering membranes in a two-step process to clean, dry, surfaces with no slope restrictions. Do not install when air temperature is within 3oC (5oF) of the dew point.

    - Sealant: "Sikaflex® 1a" by Sika, polyurethane, 1 component sealing compound.

    - Tape: "Sikalastomer-65" by Sika, isobutyl, colour white, 3 mm (1/8") thick x 19 mm (3/4") wide.

    - Base Fixation: “Sarnabar” by Sika, 14-gauge, roll-formed steel bar punched with 6 mm (1/4”) holes every 25 mm (1”) o.c. or “Sikaplan Disc.

    - Roof Walkway: Supply “Sarnatred V, or Crossgrip XTRA” by Sika Sarnafil at locations shown.

    - Perimeter Warning Membrane: “Perimeter Warning Membrane” by Sika, 100 mm (4”) wide x 30 m (100ft.) long, Sarnafil G410 membrane, colour Yellow. Perimeter Warning Membrane is hot air welded to the top of the roofing membrane in the required areas.

    - PVC Metal Flashing: Sarnaclad” by Sika, .607 mm (24 ga), G90 galvanized metal sheet with a 0.5 mm (20 mil) unsupported Sarnafil formulated membrane laminated to one side.

    - Additional Roofing Accessories: As required, refer to manufacturers published specifications and details, by Sika

- EXECUTION

  - EXAMINATION

    - Verification of Conditions:

      - Report any defects or irregularities in roof deck detrimental to roof application. Do not proceed until corrected.

      - Check deck is properly installed, with required slopes to attain positive drainage and drains are connected.

      - Ensure openings, walls and projections through deck are completed and affixed and reglets and nailing strips are in place prior to membrane installation. Cooperate with mechanical and/or electrical divisions as necessary.

      - Ensure deck substrate scheduled to receive roof system is smooth, dry, clean and free of sharp projections and of sufficient strength to withstand construction traffic and equipment.

      - Ensure plywood and lumber nailer plates and parapets are installed and secure as shown. Verify sleeves, anchors and other items to be secured to or to pass through roof membrane are installed. Verify that units and curbs are properly secured in place.

    - Evaluation and Assessment: Commencement of work implies acceptance of previously completed work.

  - PREPARATION

    - Surface Preparation:

      - Immediately before any roofing materials are applied, clean deck in accordance with roofing manufacturer's recommendations. Remove ice and snow and dry decks. Do not use salt or calcium to remove snow or ice.

      - Do no roofing work during rain, fog, sleet or snow, or upon surfaces covered with dust, water, dew, ice, frost, snow and similar detrimental conditions.

      - Before commencing work, ensure environmental and site conditions are suitable for installation of material in accordance with manufacturer's recommendations.

      - Prevent debris from blocking drain pipes during work of this Section.

    - Structural Deck:

      - Deck shall be manufactured and installed in accordance with the manufacturer's requirements, industry standards and the National Building Code of Canada (NBBC) or local code requirements.

      - Steel, minimum .793 mm (22 ga), 230 MPa (33.4 KSI).

      - Wood, minimum 38 mm (1.5") plank or minimum 19 mm (¾") exterior grade plywood sheathing.

      - Poured Concrete, minimum 20 MPa (3000 psi).

        - The surface shall be dry and free of moisture, have a level finish, and shall be free of dust, excess moisture, oil-based curing agents and loose debris. Under no circumstances shall a sealer be used in lieu of a curing agent.  Sharp ridges or other projections above the surface shall be removed before roofing.  A concrete surface profile CSP 3 to CSP 6 is required.  Achieve concrete surface profile in accordance with the ICRI Technical Guideline No. 310.2R-2013.

      - Precast Concrete,

        - The surface shall have a smooth and level finish and shall be free of dust, moisture, oil or loose debris.  All joints between precast units shall be grouted.  Any differentials in height between precast units shall be feathered for a smooth transition.  Sharp ridges or other projections above the surface shall be removed before roofing.  Panels shall be secured to structural supports as recommended by deck manufacturer.

  - INSTALLATION

    - Perform work per roof membrane manufacturer's printed installation instructions for the specified system, per CRCA’s "Roofing Specifications” manual, "FM" and "ULC" requirements and as specified herein.

    - Do not phase roofing installation. Install complete roof system on a daily basis, including flashings.

- Verify whether this applies to your Project. This is a common approach on industrial buildings, warehouses or storage buildings where thermal barrier is not required and/or sprinklers are provided.

    - Vapour Retarder Directly over Metal Deck: Install vapour retarder so it provides continuous barrier. Overlap and seal to adjacent air/vapour barrier at top of parapets and curbs to ensure air/vapour barrier continuity of building envelope. Install vapour retarder under blocking and onto vertical surfaces to meet wall air/vapour barrier and seal with fire retardant adhesive. Completely seal vapour retarder at terminations, obstructions and penetrations to prevent air movement into roofing system.

- Verify whether roof sheathing applies to this Project.

    - Roof Sheathing on Deck:

      - Place roof sheathing with long axis of each sheet transverse to ribs, with end joints staggered and fully supported on ribs. Butt boards together to moderate contact. Adjust spacing so screws are centred on ribs.

      - Hold roof sheathing in-place as required by site conditions until covered by complete roof system.

      - Temporarily cover roof sheathing not covered by membrane at the end of each Day's Work with polyethylene film.

    - Vapour Retarder over Roof Sheathing: Install vapour retarder so it provides continuous barrier. Overlap and seal to adjacent air/vapour barrier at top of parapets and curbs to ensure air/vapour barrier continuity of building envelope. Repair punctures of vapour retarder caused by subsequent work.

    - Roof Insulation [and Insulation Overlay Board]:

      - Before laying any roof insulation, inspect vapour retarder and repair any damage, if any.  Ensure surface is free of wrinkles, air pockets, fishmouths or tears.

      - Use full size insulation boards wherever possible and minimum half boards at abutting vertical surfaces. Place insulation in tight contact at joints between boards and at abutting surfaces. When cutting insulation board, cut completely through board thickness and trim to provide plain butt joints; do not break or tear insulation board to fit detail. Any areas of insulation system having voids will be rejected.

      - Do not lay more insulation than can be completely covered as a finished roofing system on the same Day. Install insulation board in straight parallel rows with long side at right angle to flutes of steel deck.

      - Stagger end joints of base layer insulation minimum 50%. Cut ends of base layer insulation units as required to provide minimum 50 mm (2") edge bearing on ribs of roof deck. Verify roof deck type and rib spacing with metal roof deck manufacturer prior to ordering insulation. [Install insulation and overlay board over base layer insulation and offset joints from underlying base layer. Top layer insulation or overlay board to be installed in soldier pattern].

      - Provide cut-offs by turning back vapour retarder sheet, or otherwise, at the exposed edges of insulation at roof edges and vertical surfaces.

      - Reduce thickness of insulation at roof drains by 13 mm (1/2") for a distance of 600 mm (24") from drain.

      - At steel roof deck, install insulation in flutes to support insulation where its thickness is reduced at roof drains.

      - Trim insulation [and insulation overlay board] to provide plain butt joints at perimeter of insulation, at copings, parapets, curbs, drains and where insulation meets a vertical surface passing through roof.

      - Do not let roof insulation [and insulation overlay board] become wet or damp during storage or installation.

    - Place Sarnaplate and Sarnafastener at spacing and patterns required to meet wind uplift requirements. Set self-drilling screws with torque controlled screwdriver so not to crush insulation or strip substrate penetration.

    - Secure overall insulation assembly [including insulation overlay board] through vapour retarder into steel roof deck with screw and plate type fasteners as specified.

    - Fasten insulation to resist uplift pressure at corners, perimeter and field of roof.

    - Roofing Membrane:

      - Unroll prefabricated sheet membrane and draw tight without folds or wrinkles. Lap side joints minimum 127 mm (5.5") for welding.

      - Attach Sarnafastener and Sikaplan Disc at specified intervals a 75 mm (3") from edge of roof membrane; as per Sika’s published specifications, details and application guides.

      - Fasten roof membrane to resist uplift pressure at corners, perimeter and field of roof.

      - Membrane overlaps shall be shingled with the flow of water where possible.

      - Roof membrane shall be fastened perpendicular to the direction of the steel deck flutes, wood plank, or precast concrete where possible.

      - Tack welding of membrane for purposes of temporary restraint during installation is not permitted and may result in voiding of Sika warranty.

      - Refer to and comply with membrane manufacturer's welding equipment requirements and induction welding techniques.

    - Membrane Flashings:

      - Install flashing membrane flashings to vertical substrates, horizontal coping substrates and other vertical projections from roof including to roof accessories per reviewed Shop Drawings, in accordance with manufacturer's published specifications, details and application guides.

      - Avoid any adhesive at lap area. Clean as necessary. Heat weld laps. Cut and weld interior corners and mitres as required. Overlap flashings at least 75 mm (3”) onto roofing membrane and heat weld to produce a tight seal.

    - Install mechanical / base fixation according to the detail drawings, manufacturer’s specifications and details with approved fasteners and plates or bars at all transitions from horizontal to vertical plane (e.g. the base of parapets, walls, curbs, peaks and valleys).

    - Expansion Joint:

      - Install insulated flexible flashing joint within the roof construction, including curb-to-wall and curb-to-curb expansion joints, in accordance with manufacturer's published specifications, details and application guides.

    - Roof Drains:

      - Install roof drain centred in depressed area of roof sump, in accordance with manufacturer's published specifications, details and application guides.

    - Roof Accessories: Install prefabricated miscellaneous roof accessory units in accordance with manufacturer's published specifications, details and application guides.

  - SITE QUALITY CONTROL

    - Site Tests and Inspections:

- Verify whether Cash Allowance includes allowance for inspection.

      - Consultant may appoint an independent roofing inspection company. Cost of inspection will be paid from Cash Allowance specified in Section 01 20 00.

      - If so, required by inspection company, or by Consultant, make any cut tests required. Costs of such tests and making good afterwards to roofing to be paid by this Subcontractor.

      - Inspection - Roof Levels:

        - Before roofing is commenced, inspect and check roof surfaces for levels.

        - Undertake a series of spot levels to determine if there is any unevenness in roof decks which may result in pools of water being left on completed roofing in excess of 13 mm (1/2") depth.

        - Ensure deck has been inspected and approved by Consultant prior to start of roofing work.

      - Check completed single ply membrane welds for continuity after cooling by use of a screwdriver run along welded seam. Ensure joints indicate an uninterrupted extrusion of melted material from joint. Ensure seams are exposed for inspection. Cut edge sealant is not permitted at any time.

      - Inspect completed membrane and flashings for punctures, tears and discontinuous weld seams. Apply additional layer of membrane over punctures and tears, extending minimum 50 mm (2") beyond damaged area in any direction and heat weld. Re-weld seams where necessary.

  - PROTECTION

    - Provide adequate protection of materials and work of this Section from damage by weather, traffic and other causes. At the end of each Day's work provide temporary water cutoff between finished roofing membrane and roof deck substrate to prevent weather damage and water from entering finished roof assembly. Remove such temporary cutoff strip completely prior to commencing with work.

- For most of our Projects 13 mm (1/2") thick board is sufficient. For large Projects having lots of roof traffic use 19 mm (3/4") thick plywood.

    - Provide protection covering out of 13 mm (1/2") [19 mm (3/4")] thick plywood underlaid with 25 mm (1") thick polystyrene insulation board adhered to it, over roofed areas when working from, or over, such roof surfaces. Ensure to place a separator sheet between temporary protection covering roof membrane. Provide such protection below hoist rigs, ladders, pallets of material and in other circumstances where the roofing membrane is exposed to potential damage. Secure protection boards mechanically against windstorm loss.

    - Temporarily block drain pipes during application of roofing membrane. Remove blocking each night or when work is not in progress and after work of this Section is completed.

    - At conclusion of each Day's work, seal exposed edges of roof insulation. Remove when resuming work.

    - Protect work of other trades from damage resulting from work of this Section. Make good such damage at no cost to Owner.